# Fiber Installation

Dan Conroy| Infrastructure Technician |

# Planning

A ticket was raised with us as a user had an issue that required us to install a fiber cable for them. This was needed in order for the customer to complete a project that they were working on.

In order to complete this job we first had to understand what the customers’ needs where and what we needed to do to meet them. The customer needed us to run a fiber cable from their private server to a secure lab. The customer supplied the fiber cable which they wanted us to install, the cable that the customer wanted us to install was OM3 Multi-Mode Fiber.

The first thing that we had to plan was where we were going to run the fiber to get it from the server to the ports that were in the customers secure lab. This was important as we had to get the fiber across two corridors, in order to do this we choose to go through the ceiling. We choose the ceiling as there was another fiber cable that was already in place this one went form the private server to the secure lab however this fiber cable went to the other end of the secure lab. This meant that there was already a cable tray in place that was used for this fiber cable. It also meant that we could use the route that the other fiber cable had taken and follow that. We were also able to see how they fastened down the cable to keep it secure, we were then able to plan to fasten it down at the same point so it keeps everything professional and it also keeps both installs the same. Meaning that if we need to take out the fiber cables we can unclip the ties that hold the fiber in place at the same points as the other fiber cable making it a lot easier to take out both cables.

We then had to get the unique identifying numbers for the ports and the cables. This is so we can put the numbers onto a piece of software that allows us to map each of our servers and we can then show what is connected to each port and where the wire connects to on the other side.

We then had to plan when we were going to install the cable as it was all inside of a secure area that we did not have access to. This meant that we had to agree a time with the customer that they could let us into the secure area. We also had to agree a time when the customer could shut down all of the live kit that they had in the lab so we could install the fiber cable.

# Execution

The first thing the we did when we where installing the fiber cable was we put signs out in the corridors alerting people that we were working, this was especially important as we would be taking down the ceiling panels and we would also be using ladders.

We then removed the ceiling panels and placed them in a store room just off the corridor we were working on just to make sure that nobody would trip over and hurt themselves. We then set the step ladders up so that we could check the cable trays and make sure that they are ok and securely fastened to the wall.

We then reeled off  the required amount of OM3 fiber cable from the cable reel and we made sure that we had more than was required in case we made any mistakes.

We then ran the cable from the secure lab to the private server room via the ceiling cable trays. Once the cable sat in the tray correctly we secured it to the cable tray and put the roof panels back in place. Once this was done we put away the step ladders so they were not a danger to anybody.

We then went into the secure lab and got the fiber cable and equipment ready to splice the fiber cable. The first thing that I did was I striped the cable of its plastic case. Then I removed the kevlar strands from the collection of fiber cables. I then separated the fiber cables and put them into the order that I would splice them. Once I had separated them I got the correct amount of pig tails to match the amount of fiber cables. I then put the heat protectors onto the pig tails, I then striped the individual fiber cables. I then wiped the fiber, cleaved it and put it into place in the fiber splicer I then striped the end of the pig tail, wiped and cleaved it. Then I put it into the fiber splicer. Once both the fiber cable and pig tail were in place in the fiber machine, I lined them up using the fiber splicing machine and fused them together. I then took them out of the splicer and put them into the heater with sets the heat protector in place over the weaker unprotected area of the cables that had just been fused.

Once I had done the above for all of the fiber cables that were required for the sockets. I went into the server room and repeated the process for the fiber optic patch panel.

Once both the patch panel and the sockets had been patched I tested each port on the patch panel and each socket. Using fluke testers to make sure that there were no faults in any of the fiber cables or in any of the connections or splices that I had done.

Once I was happy with the installation I went and got the customer and made sure that they were happy with everything that I had done. Once they were content with my efforts I closed the call.

# Problems encountered during the execution

During the execution this job we only encountered one problem, which was when we were installing the fiber cable into the server room there was no draw rope in the PVC pipe that connected the cable tray to the bottom of the server. This PVC pipe runs through the wall in the server room. In order to get the fiber cable through without damaging it we had to force a makeshift drawstring through the PVC pipe. Once this was in we were able to pull our fiber cable through without any issues. We had also attached a new draw rope to the top of our fiber so we could put in a new draw rope just in case they needed another connection putting in.

# Conclusion

We completed the job successfully despite the problems that we encountered, and resolved the customers problem which was that they could not complete a project that they were working on without a fiber cable. The customer was very happy with the work that had been done and the speed at which we had completed the job. We spent 6 hours completing the job and successfully finished it in one day.

From this job I was able to get some more hands on experience with installing fiber cables and splicing them. I was also able to get some more practice at splicing the fiber cables. This job also allowed me to get more familiar with the process that are set out by my companies policy’s and guide lines.